## UltraLevel_Pro_V04
Address | Parameters | Data Format | Command
40001 | Level in Liter | HEX | R
40002 | Level in mm | HEX | R
40003 | Level in Per % | HEX | R
40004 | 2ND Level in Liter | HEX | R
40005 | 2ND Level in mm | HEX | R
40006 | 2ND Level in % | HEX | R
40007 | Alarm | HEX | R
40008 | ADC Voltage | HEX | R
4009-11 | MAC Address | HEX | R
40012 | Version | HEX | R
40013 | Power Supply Voltage | HEX | R
40014 | Temperature 1 | HEX | R
40015 | Temperature2 | HEX | R
40016 | Settings | HEX | R/W
40017 | Low Level Realy in mm | HEX | R/W
40018 | High Level Realy in % | HEX | R/W
40019 | LPH | HEX | R/W
40020 | 0% "0V Triming Point" | HEX | R/W
40021 | 100% "4V Trimming Point" | HEX | R/W
40022 | Damping "turbulence reduction" | HEX | R/W
40023 | Level Calibration offset " Constant " | HEX | R/W
40024 | Sensor offset | HEX | R/W
40025 | Tank offset | HEX | R/W
40026 | Tank Type | BINARY | R/W
40027 | Tank Height | HEX | R/W
40028 | Tank Widht | HEX | R/W
40029 | Tank Length | HEX | R/W
40030 | Tank Diameter | HEX | R/W
40031 | Salve ID | HEX | R/W | 40100
40032 | Baud Rate | BINARY | R/W
No Linear Tank Data
40501 | 1 MM | HEX | R/W
40551 | 1 Liter | HEX | R/W
Settings 40014 | Default : In mm |  | LSB
| In mm | 1 | 1
| In CM | 0
| Temperature Sensor Enable | 1 | 2
| DAC 0-4V | 1 | 4
| Switch O/P Low & High | 1 | 8
| RS485 | 1 : Enable | 1
| Modbus/ Broadcast | 0 : Modbus 1: Broadcast | 2
| Radar Measurment Disable | 1: Disable Note : Save in RAM ,This is for Multiple Sensor Calibtation in Single Setup | 4
TANK TYPE 40025 | Default : Rectangle
| lookup |  | 1 | “0001”
| Rectangle |  | 2 | “0002”
| Horizontal Oval |  | 4 | “0004”
| Horizontal Cylinder |  | 8 | “0008”
| Vertical Cylinder |  | 1 | “0010”
| Vertical Capsule |  | 2 | “0020”
| Horizontal Capsule |  | 4 | “0040”
| Elliptical |  | 8 | “0080”
| NoLinear |  | 1 | “0100”
Baud Rate 40026 | Default 9600 | 8,N,1 Default
| 1200 | 0 | 1
| 2400 | 1 | 2
| 4800 | 2 | 4
| 9600 | 3 | 8
| 19200 | 4 | 1
| 57600 | 5 | 2
| 115200 | 6 | 4
Alarm 40007 |  | BINARY
| Low Level | LSB 1 | 150 | mm
| Low Low Level | 2 | 50 | mm
| High Level | 4 | 90 | %
| High High Level | 8 | 95 | %
| Fuel Filling | 1 | LPH * 2 Times increasing level
| Fuel Theft | 2 | <LPH * 1.8 Times
| Fuel Abnormal | 4 | >LPH
| Power Fail | 8
| DAC Comm Error | 1
| Radar Comm Error | 2
| RS485 Comm Error | 4
| BLE Error | 8
| low Level Relay Activated | 1
| High Level Relay Activated | 2
Broadcast
<MAC ID, "Modbus Read Data upto 4015";
IF Switch O/P Low And High Enable
Port : P0.12 for Low Level Relay
Port: P0.31 for High Level Relay
IF Temperature Sensor Enabled
Port : P0.31 for Temp1
Port : P0.29 for Temp2